ARE 346N Building Environmental Systems

Midterm I

Working time: 75 Minutes

You may use your class notes and cheat sheets that you prepared.

1			_____________	/  15

2			_____________	/  30

3			_____________	/  15

4			_____________	/  35

5 			_____________	/  30

Total		_____________	/  125

Write your name on every page as well as this one.  You can use other side of a paper if you need.

SHOW ALL OF YOUR WORK AND CLEARLY IDENTIFY POINTS AND PROCESSES IN THE ATTACHED PSYCHROMETRIC CHART.

1. SHORT QUESTIONS (15 pts total - 1  pt each)

Answer True or False for the following questions:

1. Cooling load is the energy consumption during the summer period.         	 True     False

2. With the increase of outdoor air temperature the COP of heat pump decreases.   True     False

3. Condenser in a chiller is always cooled by air.                 				 True     False

4. Evaporator in DX cooling machine always cools the water.			 True     False

5. For evaporative cooling we need water. 						 True     False

6. TETD depends on thickness of the wall.                                                                 True     False

7. Low-e window has higher conductivity than regular window.                         	 True     False

8. Shading coefficient (SC) is unitless.                    					 True     False

9. Overall carbon emission is larger with electric heating or with coal base heating. True     False

10. When sizing heating equipment you need to include solar radiation.  		  True     False

11. VAV system can reduce humidity in the building.				 True     False

12. VAV with reheaters is more energy efficient than VAV without reheaters.     	 True     False

13. Steam pipe line is more efficient way to transport the energy than air duct.       	 True     False

14. All furnaces need to be vented.       						 True     False

15. Mean radiant temperature affects thermal comfort. 				 True     False

2. HVAC SYSTEMS (30 pts total)

a)    2 points

Name the major advantage of using high pressure water as a heat transfer fluid in a heating system and the major advantage of using air?

Advantage of using high pressure water:

Advantage of using air:

b)   3 points

Indicate the smallest and largest quantity from the following (all destruction system below need to transport the same amount of energy):

-   The pipe diameter for low pressure hot water heating system,

-   The pipe diameter for high pressure hot water heating system,

-   The pipe diameter required for a low pressure steam heating system

-   The pipe diameter required for high pressure steam heating system

-   The duct diameter required for an air heating system

c)    4 points

Write at least 5 mechanisms for heat exchange of human body with surrounding environment:

1________________________

2________________________

3________________________

4________________________

5________________________

Indicate the most significant one.

d)   4 points

What is the major difference between Variable Volume (VAV) and Constant Air Volume (CAV) air delivery systems?

Write one advantage and one disadvantage for using these systems:

VAV                                        CAV

Advantage             ________________________          ________________________

Disadvantage        ________________________          ________________________

e)   7 points

Explain the principle of operation of VAV system. (Use your schematic)

f)   4 points

Could we use the cooling tower in absorption chiller?

- yes, we can use it to cool the condenser

- no because the absorption chiller always uses air cooled condenser

- no because in the he absorption chiller uses steam as the energy source

What is the advantage of absorption chiller over vapor compression chiller?

In which situation would you use absorption chiller (1-2 sentences)?

g)   6 points

Use the schematic below to explain how the chill water storage tank operates.

(Show the water circulation path and explain it.)

Why we use water storage tanks with chillers?

3) COOLING and HEAT- PUMP CYCLES (total 15 points)

a) 5 points

When you use heat pump for heating in winter and cooling in summer, what is the purpose of evaporator in 1) winter condition and 2) in summer condition?  (1-2 sentences)

b) 3 points

In summer period (cooling operation of your air-conditioner), with the decrease of indoor air temperature the efficiency of the air-conditioner

- increases

- decreases

- stays the same

c) 7 points

Explain your previous answer (from part b) using the schematic below and your knowledge about vapor compression cooling.

Comment how will this affect the electric energy consumption for cooling. (2-3 sentences).

4) Psychrometrics and Air-conditioning - Total 35 points

Use the psychrometric chart to define the following process in an air handling unit.

250 CFM of outdoor air OA (T=35°F, RH=60%) is mixed with 750 CFM of recirculated air RA(T=70°F, RH=50%). The mixture (M) is then heated by heater to H(T=105°F). Then, the air is humidified by a stream humidifier to H(RH=20%).

b) 15 points

Draw the process in the attached psychrometric chart.

a) 5 points

Is this the winter or summer air conditioning?

Do you increase or decrease humidity in the room by supplying air with condition H? Why?

c) 15 points

- Find the amount of water added by steam humidifier.

- How much energy you need to boil this amount of water.

- Find the sensible and latent energy added by heater.

5) LOAD CALCULATION Total 30 points

A zone in a skyscraper consists of a single office with a glass wall (window) from one side and from the other five sides the office is surrounded by rooms with the same indoor temperature. Outdoor design dry-bulb temperature is 34°C and design WBT=25°C. The inside design conditions are 24°C and 50% RH.

The U-value for the glass wall is 2 W/(m2K) and there is 10m2 of this glass wall.

The glass is heavily tinted SC=0.4 and the SHGF for the critical hour is 250W/m2. There are 500 W of sensible internal gains and 200W of latent internal gains.

There are no other heat losses or gains from the space (no infiltration).

There is a requirement for 0.04 m3/s of outdoor air for ventilation (VOA) that is supplied through an air conditioning system.

a) 15 points

Calculate the cooling load of the zone (without ventilation).

b) 5 points

Calculate the cooling load from ventilation.

c) 10 points

If the temperature of supply air is 14°C, how much supply air (VSA) is needed.

How much recirculate air is needed in this zone VRA=?

# Text boxes

External air