General strategies for cooling and heating loads:

Heating Loads:

- Calculate ∑ UA (for slab edge ∑ FP and for infiltration/ventilation ∑ mcp) of items on first page

to get an answer in BTU/(hr °F) or W/°C.

- Multiply by design temperature difference.

- The result is your raw uncorrected heating load [BTU/hr] or [W].

Cooling Loads (all steps should be in [BTU/h or W]):

- Calculate cooling load from conduction through opaque surfaces using one of three methods on (TETD, CLTD, Te) second page.

- Add solar gain through windows.

- Add sensible internal gains and infiltration.

- The result is your raw sensible cooling load.

- Calculate latent internal gains.

- Calculate latent gains due to infiltration.

- The sum of 5 and 6 is your raw latent cooling load.

Heating (Sensible only)

|  | Formula | Strategies | ASHRAE1 | Other2 | Textbook3 |
| --- | --- | --- | --- | --- | --- |
| Walls (subtract window/door areas) | Q = UAΔT | Calculate U Values of assembly from wall components | 25.2 – 25.12 25.Table 4 |  | Table 2-3A |
|  |  | Look up assembly values | Some examples in chapter 25, below grade walls 25.14-25.15 | Ecotope report | Table 2-14 (last column is U-Value in BTU/(hr°F ft2) |
| Windows/Skylights (use rough opening area, frame type very important) | Q = UAΔT | Look up U Values in NFRC guide or default tables | 27.Table 5 30.Table 4 | NFRC Certified Products Guide | Examples in Chapter 2 |
| Roof (subtract skylight areas) | Q = UAΔT | Calculate U Values of assembly from wall components | 25.Table 4 Attic space - 25.Table 5 |  | Table 2-3A |
|  |  | Look up assembly values | Some examples in chapter 25 | Ecotope report | Table 2-12 |
| Doors (use rough opening area) | Q = UAΔT | Look up U Values | 25.Table 6 30.Table 6 | NFRC Certified Products Guide (for doors with glazing) | Examples in Chapter 2 |
| Slab/Foundation edge | Q = FPΔT | Look up F Value and multiply by perimeter, P | 25.14 - 25.15 | Ecotope report | Table 2-10,2-11 Be careful |
| Infiltration | Q = mcpΔT | m = ρV | 26.24, 27.7 |  | Tables 2-8 |
| Ventilation | Q = mcpΔT | cp = 0.24 BTU/(lb °F) or 1007 J/kg K | 26.16-26.18 26.Tables 3-6 | ASHRAE Standards 62, 62.2 | Table 2-9A |
| Weather Data (elevation, latitutde) | ΔT | Use comfort zone for appropriate indoor conditions and 99% dry-bulb for outdoor temperature. | 27.Tables 1A,2A,3A |  | Tables 2-2A,2-2B,2-2C |

1ASHRAE 2001 Fundamentals. Chapter.page number or Chapter.Table number

2NFRC Certified Products Guide http://www.nfrc.org/nfrcpd.html, Super Good Cents Heat Loss Reference Manual by Ecotope Inc on class website

3Tao and Janis. 2004. Mechanical and Electrical Systems in Buildings. 3rd Ed.

Cooling Load Additions (sensible and latent)

|  | Formula | Strategies | ASHRAE1 | Other2 | Textbook3 |
| --- | --- | --- | --- | --- | --- |
| Conduction through opaque surfaces | Q = UA×TETD | Use tables to determine Total Equivalent Temperature Difference |  |  | Tables 2-13 |
|  | Q = UA×CLTD | Use Tables to determine Cooling Load Temperature Difference | 28.Tables 1 and 2 |  |  |
|  | Q = UA(Te-Tin) | Calculate Sol-Air Temperature | 29.15-29.16 |  |  |
| Solar gain through Windows/Skylights | Q = GLF×A | Look up Glazing Load Factors | 28.Tables 3 and 4 |  |  |
| (watch for shading, dirty windows, shades and blinds, etc.) | Q = U A×ΔT + A×SHGF×SC | SC=SHGC/0.87 | SFGF 30.Table 13 1997 Fundamentals Table 29 -51 SHGC – 30.Table 19, 28.Table 5 | SHGC - NFRC Certified Products Guide | SHGF,SC - Table 2-15A, 2-16 |
| Sensible Infiltration/ventilation | Same like Heating |
| Sensible Internal Gains | Q= ΣQi | Include people, lights, appliances | 29.Tables 1,2,3,5-15 |  | Table 2-17 |
| Latent Internal Gains | Ql = ΣQi | Include people, appliances, moisture sources | 29.Tables 5-15 |  | Table 2-17 |
| Latent Ventilation/ Infiltration | Ql = mhfgΔw | hfg = hig from ASHRAE 6.Table 3 | 26.16-26.18 26.Tables 3-6 | ASHRAE Standards 62, 62.2P | Table 2-8 and 2-9A |
| Weather Data (elevation, latitutde) | ΔT, Δw (you will need to use psychrometric chart to get indoor and outdoor humidity ratios) | Use comfort zone for indoor conditions and 1% dry-bulb and coincident wet-bulb for outdoor conditions. | 27.Tables 1A,2A,3A |  | Tables 2-2A,2-1B,2-2C |

1ASHRAE 2001 Fundamentals Chapter.page number or Chapter.Table number

2NFRC Certified Products Guide http://www.nfrc.org/nfrcpd.html, Super Good Cents Heat Loss Reference Manual by Ecotope Inc on class website

3Tao and Janis. 2004. Mechanical and Electrical Systems in Buildings. 3rd Ed.